## Slide 1: Boiler Blow down use case Updated [22nd Dec 2021]

## Slide 2
Boiler optimization analysis - Outcomes
SCOPE : Analyze & Optimize the Boiler Blow Down Rate by measuring Near Real-time quality parameters from Feed water, Drum water and Steam & optimize the chemical dosages as per SOP to improve the Boiler efficiency
Outcomes: Optimizing Chemical Strokes [Continuous and batch] at right time with right Qty of chemical dosage to control the optimized CBD/IBD for Boiler efficiency
      Deriving quality parameters from Operation & Conductivity parameters [feed-water, drum water & Steam]
      Appropriate Chemical Strokes & Blow-down recommendation with Qty - Batch & Realtime

## Slide 3
Data Availability & Scope
Day Wise Data : Water flow rate, At-temperature water flow, blow-down%, Fuel consumption, Steam temp & Pressure, Chemical dosage consumption
Shift-wise Data : Manual quality measures at feed water, Drum water and Steam
Minute Wise Data : Conductivity Sensor Data at feed water, DM and Steam
Shift-wise Data : Chemical Dosage consumed by continuous flow scheduled at Feed water [Morpholine, DEHA] & TSP at Drum Water
Available Data
Expected Data
Shift-wise data preparation and availability would increase the accuracy of outcome analysis
Adding conductivity data would add the accuracy of prediction – quality measures

## Slide 4
Boiler Process
Feed Water/90% recycle
Makeup Water 10%
Steam
Feed – pH, Silica, R-DEHA& Silica
DM – pH, Phosphates & Silica
Steam - Silica
DEHA
Cont. Chemical Addition
Batch - Chemical Strokes
Cont. Blow Down
Intermittent Blow Down
Turbine
Gas Combustion
Feed Water
Drum Water
Steam Drum
Optimization point / Control Operators
Boiler
Water Re-cycle
Wastage
Morpholine
TSP
Quality parameters
8Hr quality Data for Dosage & Blow down Control

## Slide 5
Boiler optimization analysis – Scope & Outcomes
Blow Down optimization Scope[Feed water, Drum Water & Steam] | Input Parameters | Expected Outcomes | Challenges | Approach
Dosage Qty optimization @Feed water. Compute Accessing Feed water quality data [pH, Conductivity, DEHA & Silica] at Near real time to decide the Chemical Stroke with right optimized proportion | Batch : pH, Conductivity, DEHA & Silica Real-time : Conductivity | Triggering Optimized Chemical Stroke in Near real-time | No real-time quality data except the Conductivity No historical chemical stroke transaction with Qty | Deriving near-real time quality data using sensor provided real-time conductivity – Designing Soft Sensors using Algos
Dosage Qty optimization @Drum Water. Basing on Conductivity measure , compute other quality parameters [pH, Conductivity, Silica & Phosphate] & provide the Chemical Stroke with right optimized proportion along with possible increase in CBD or initiation of IBD | Batch : pH, Conductivity, Silica & Phosphate Real-time : Conductivity | Triggering Optimized Chemical Stroke & CBD/IBD in Near real-time | No real-time quality data except the Conductivity No historical chemical stroke transaction with Qty | Deriving near-real time quality data using sensor provided real-time conductivity – Designing Soft Sensors using Algos
Dosage Qty optimization @Steam. Basing on Conductivity measure, compute other quality parameter [silica] & provide the possible increase in CBD or the initiation of IBD | Batch: Silica Real-time : Conductivity | Triggering Optimized CBD/IBD in Near real-time | No real-time quality data except the Conductivity | Deriving near-real time quality data using sensor provided real-time conductivity – Designing Soft Sensors using Algos

## Slide 6: List of Tasks
  Data Preparation.
  EDA – Uni & Bi Variate Analysis.
  Interpretation.
  Quality parameters has gone out of the threshold.
  Predict the Quality Parameters for Feed Water - pH, Silica.
  Predict the Quality Parameters for Drum Water - Silica, PO4.
  Predict the Quality Parameters for main stream - Silica.
  Model Building.

## Slide 7: Final Dataset
Integrated all the data set with the time-line of day wise
Removed the IBR Shutdown rows in the given dataset.

## Slide 8: Feed Water EDA – Bi Variate Analysis
Feed water and Attemperator feed are in positive correlation
Increase in conductivity will decrease the pH value in feed water

## Slide 9: Feed Water EDA – Uni Variate Analysis.
No variance of Silica level in Feed water – Mostly consistent
Silica level is in increasing trend from Feed water, DM and Steam

## Slide 10: Drum Water EDA – Uni Variate Analysis
NA value is being replaced with median.
In Drum Water pH there are many outliers in the dataset.
Lower range is 8.55
Upper range is 10.11

## Slide 11: Drum Water EDA – Bi Variate Analysis.
Feed water increase & Attemperator Feed water are directly proportionate. In value of correlation can take any values from -1 to 1.
Feed water and Attemperator variable are positively correlated.
In Drum Water PO4 there are many outliers in the dataset – PO4 in high variations, Lower_range is 3.11 & Upper_range is 24.79

## Slide 12: Main Steam EDA – Uni Variate Analysis.
Silica levels are varying in Steam [0.01 to 0.04].
Main stream pH is increase based on the feed water pH value.

## Slide 13: Main Steam EDA – Bi Variate Analysis
Feed water and Attemperator variable high positive correlation(0.94).
Main steam silica and feed water silica positively correlation(0.39)
There is a peak in Silica value on 14th Aug 2020 – 0.04

## Slide 14: Chemical compounds
Heavy usage of Morpholine dosage (May – August)
Heavy usage of TSP dosage
(April – November)

## Slide 15: Chemical compounds
Heavy usage of DEHA dosage (April – October)

## Slide 16: Chemical compounds
There is no proper Measure for Chemical Dosage at specified interval

## Slide 17: Uni – Variate Table for all the parameters
Outlier to be identified

## Slide 18: Next steps
Baseline the Boiler efficiency by capturing quality parameter deviation Vs Chemical Dosage consumption - due to time delay
Baseline the Boiler efficiency by capturing quality parameter deviations Vs Blow down %
Measuring Chemical dosage savings against the quality parameter optimization [Remedy at right time]
Measuring Blow-down % savings against the quality parameter optimization at right time